1.0 General

1.1 - Air filters shall be HEPA-grade high-capacity air filters with waterproof micro glass fiber media, tapered corrugated aluminum separators, urethane sealant, 16-gauge steel enclosing frame, and one of the following: a poured-in-place seamless gasket, dovetail-cornered peel-and-stick neoprene gasket or gel seal.

1.2 - Sizes shall be as noted on drawings or other supporting materials.

2.0 Construction

2.1 - Filter media shall be one continuous pleating of micro glass fiber media.

2.2 - Pleats shall be uniformly separated by tapered corrugated aluminum separators incorporating a hemmed edge to prevent damage to the media.

2.3 - The media pack shall be potted into the enclosing frame through the use of a urethane sealant.

2.4 - The enclosing frame of 16-gauge steel with a zinc aluminum alloy finish, shall be bonded to the media pack to form a rugged and durable enclosure. The filter shall be assembled without the use of fasteners to assure no frame penetrations. Overall dimensional tolerance shall be correct within -1/8”, +0”, and square within 1/8”.

2.5 - A (poured-in-place seamless gasket, dovetail-cornered peel-and-stick neoprene gasket or gel seal) shall be included on the downstream side of the enclosing frame to form a positive seal upon installation.

3.0 Performance

3.1 - The filter shall have a tested efficiency of (99.97%, 99.99%, and 99.999%)* as defined by IEST RP-CC001.

3.2 - Initial resistance to airflow shall not exceed 1.35” w.g. +/-10% at rated capacity.

3.3 - Filter shall be rated by Underwriters Laboratories as UL-900 and UL-586.

3.4 - The filter shall be capable of withstanding 10” w.g. without failure of the media pack.

3.5 - Manufacturer shall provide evidence of facility certification to ISO 9001:2015.

Supporting Data - The filter shall be labeled as to tested efficiency, rated/tested airflow, and pressure drop and shall be serialized for identification.

Filters shall be Camfil Absolute XH or equal.

* Items in parentheses ( ) require selection.

Sept/2024